199—21.7 (476) Standards of quality of service.

21.7(1) Pressures. Under normal condition of water usage the pressure (pound per square inch gauge) at a customer’s service line shall be not less than 25 PSIG and not more than 125 PSIG.

At regular intervals, a utility shall make a survey of pressures in its water system. The survey shall be of sufficient magnitude to indicate the quality of service being rendered at representative points on its system. Survey should be conducted during periods of high usage at or near the maximum usage during the year. The pressure charts for these surveys shall show the date and time of beginning and end of the test, and the test location. Records of these pressure surveys shall be maintained at the utility’s principal office in the state and made available to the board upon request.

21.7(2) Interruption of supply.

a.   	 A utility shall make a reasonable effort to prevent interruptions of service. When an emergency interruption occurs the utility shall reestablish service with the shortest possible delay consistent with the safety to its customers and the general public. If an emergency interruption affects fire protection service, the utility shall immediately notify the fire chief or other responsible local official.

b.   	 When a utility finds it necessary to schedule an interruption of service, it shall make a reasonable effort to notify all customers to be affected by the interruption. The notice shall include the time and anticipated duration of the interruption. Interruptions should be scheduled at hours which create the least inconvenience to the customer.

c.   	 A utility shall retain records of interruptions for a period of at least five years.

21.7(3) Supply shortage. The utility shall attempt to furnish a continuous and adequate supply of water to its customers and to avoid any shortage or interruption of water delivery.

a.   	 If a utility finds that it is necessary to restrict the use of water, it shall notify its customers, and give the board notice, before the restriction becomes effective. The notification shall specify:

(1) 	 The reason for the restriction.

(2) 	 The nature and extent of the restriction.

(3) 	 The effective date of the restriction.

(4) 	 The probable date of termination of the restriction.

b.   	 During the times of threatened or actual water shortage, the utility shall equitably apportion its available water supply among its customers.