567—41.6 (455B) Disinfection byproducts maximum contaminant levels and monitoring requirements.

41.6(1) Disinfection byproducts.

a.   	 Applicability.

(1) 	 This rule establishes criteria under which CWS and NTNC public water supply systems that add a chemical disinfectant to the water in any part of the drinking water treatment process or which provide water that contains a chemical disinfectant must modify their practices to meet the MCLs listed in this rule and the maximum residual disinfectant levels (MRDL) and treatment technique requirements for disinfection byproduct precursors listed in 567—43.6(455B).

(2) 	 This rule establishes criteria under which TNC public water supply systems that use chlorine dioxide as a disinfectant or oxidant must modify their practices to meet the chlorine dioxide MRDL listed in 567—paragraph 43.6(1)“b.”

(3) 	 Compliance dates for this rule are based upon the source water type and the population served. Systems are required to comply with this rule as follows, unless otherwise noted. The department may assign an earlier monitoring period as part of the operation permit, but compliance with the maximum contaminant level is not required until the dates stated below.

1. 	 Surface water and IGW CWS and NTNC. CWS and NTNC systems using surface water or groundwater under the direct influence of surface water in whole or in part and which serve 10,000 or more persons must comply with this rule beginning January 1, 2002. CWS and NTNC systems serving fewer than 10,000 persons must comply with this rule beginning January 1, 2004.

2. 	 Groundwater CWS and NTNC. CWS and NTNC systems using only groundwater not under the direct influence of surface water must comply with this rule beginning January 1, 2004.

3. 	 TNC using chlorine dioxide. TNC systems are not required to comply with this rule.

(4) 	 Consecutive systems. Consecutive systems that provide water containing a disinfectant or oxidant are required to comply with this rule. A consecutive system may be incorporated into the sampling plan of the supply that produces the water (the primary water supplier), provided:

1. 	 There is a mutual signed agreement between the primary and consecutive system supplied by that primary system that states the primary system will be responsible for the compliance of its consecutive system with this rule, regardless of additional treatment by the consecutive system.

2. 	 Beginning with the primary water supply, each successive consecutive system must also be included in the primary supply’s sampling plan, so that there is no system with its own sampling plan between the primary supply and the consecutive supply covered by the primary supply’s plan.

3. 	 It is understood by the primary and all consecutive systems that, even if only one system in the sampling plan has a violation, all systems in the sampling plan will receive the violation and be required to conduct public notification.

4. 	 The department receives a copy of the signed agreement and approves the sampling plan prior to the beginning of the compliance period.

If a mutual agreement is not possible, each system (the primary system and each consecutive system) is responsible for compliance with this rule for its specific system.

(5) 	 Systems with multiple water sources. Systems with water sources that are used independently from each other, are not from the same source as determined by the department, or do not go through identical treatment processes are required to conduct the monitoring for the applicable disinfectants or oxidants and disinfection byproducts during operation of each source. The system must comply with this rule during the use of each water source.

b.   	 Maximum contaminant levels for disinfection byproducts. The maximum contaminant levels (MCLs) for disinfection byproducts are as follows:

| Disinfection byproduct | MCL (mg/L) |
| --- | --- |
| Bromate | 0.010 |
| Chlorite | 1.0 |
| Haloacetic acids (HAA5) | 0.060 |
| Total trihalomethanes (TTHM) | 0.080 |

c.   	 Monitoring requirements for disinfection byproducts.

(1) 	 General requirements.

1. 	 Systems must take all samples during normal operating conditions.

2. 	 Systems may consider multiple wells drawing water from a single aquifer as one treatment plant for determining the minimum number of TTHM and HAA5 samples required, with department approval.

3. 	 Failure to monitor in accordance with the monitoring plan required under 41.6(1)“c”(1)“6” is a monitoring violation.

4. 	 Failure to monitor is a violation for the entire period covered by the annual average where compliance is based on a running annual average of monthly or quarterly samples or averages, and the system’s failure to monitor makes it impossible to determine compliance with MCLs.

5. 	 Systems may use only data collected under the provisions of this rule or 567—43.6(455B) to qualify for reduced monitoring.

6. 	 Each system required to monitor under the provisions of this rule or 567—43.6(455B) must develop and implement a monitoring plan. The system must maintain the plan and make it available for inspection by the department and the general public no later than 30 days following the applicable compliance dates in 41.6(1)“a”(3). All systems using surface water or groundwater under the direct influence of surface water and serving more than 3,300 people must submit a copy of the monitoring plan to the department by the applicable date in 41.6(1)“a”(3)“1.” The department may also require the plan to be submitted by any other system. After review, the department may require changes in any plan elements. The plan must include at least the following elements:

● 	 Specific locations and schedules for collecting samples for any parameters included in this rule.

● 	 How the system will calculate compliance with MCLs, MRDLs, and treatment techniques.

● 	 If providing water to one or more consecutive systems, and the consecutive systems have agreed to the sampling plan by the primary supplier of the water pursuant to 41.6(1)“a”(4), the sampling plan of the primary water supplier must reflect the entire distribution system.

7. The department may require a monthly monitoring frequency for disinfection byproducts, which would be specified in the operation permit.

(2) 	 Bromate. Community and nontransient noncommunity systems using ozone for disinfection or oxidation must conduct monitoring for bromate.

1. 	 Routine monitoring. Systems must take at least one sample per month for each treatment plant in the system using ozone, collected at each source/entry point to the distribution system while the ozonation system is operating under normal conditions.

2. 	 Reduced monitoring. The department may allow systems required to analyze for bromate to reduce monitoring from monthly to once per quarter if the system demonstrates that the average source water bromide concentration is less than 0.05 mg/L based upon representative monthly bromide measurements for one year. The system may remain on reduced bromate monitoring until the running annual average source water bromide concentration, computed quarterly, is greater than or equal to 0.05 mg/L based upon representative monthly measurements. If the running annual average source water bromide concentration is greater than or equal to 0.05 mg/L, the system must resume routine monitoring required by 41.6(1)“c”(2)“1.”

(3) 	 Chlorite. Community and nontransient noncommunity water systems using chlorine dioxide, for disinfection or oxidation, must conduct monitoring for chlorite.

1. 	 Routine daily monitoring. Systems must take daily samples at the entrance to the distribution system. For any daily sample that exceeds the chlorite MCL, the system must take additional samples in the distribution system the following day at the locations required by 41.6(1)“c”(3)“3,” which are in addition to the sample required at the entrance to the distribution system.

2. 	 Routine monthly monitoring. Systems must take a three-sample set each month in the distribution system. The system must take one sample at each of the following locations: near the first customer, at a location representative of average residence time, and at a location reflecting maximum residence time in the distribution system. Any additional routine sampling must be conducted in the same manner (as three-sample sets, at the specified locations). The system may use the results of additional monitoring conducted in accordance with 41.6(1)“c”(3)“3” to meet the requirement for monitoring in this subparagraph.

3. 	 Additional monitoring. On each day following a routine sample monitoring result that exceeds the chlorite MCL at the entrance to the distribution system, the system is required to take three chlorite distribution system samples at the following locations: as close to the first customer as possible, in a location representative of average residence time, and as close to the end of the distribution system as possible (reflecting maximum residence time in the distribution system).

4. 	 Reduced monitoring.

● 	 Daily chlorite monitoring at the entrance to the distribution system required by 41.6(1)“c”(3)“1” may not be reduced.

● 	 The department may allow systems with monthly chlorite monitoring in the distribution system required by 41.6(1)“c”(3)“2” to be reduced to a requirement of 1 three-sample set per quarter after one year of monitoring where no individual chlorite sample taken in the distribution system under 41.6(1)“c”(3)“2” has exceeded the chlorite MCL and the system has not been required to conduct additional monitoring under 41.6(1)“c”(3)“3.” The system may remain on the reduced monitoring schedule until either any of the three individual chlorite samples taken quarterly in the distribution system under 41.6(1)“c”(3)“2” exceeds the chlorite MCL or the system is required to conduct monitoring under 41.6(1)“c”(3)“3” of this rule, at which time the system must revert to routine monitoring.

(4) 	 Total trihalomethanes (TTHM) and haloacetic acids (HAA5).

1. Routine monitoring. Systems must monitor at the frequency indicated in the following table:

Routine Monitoring Frequency for TTHM and HAA5

| Type of System (source water type and population served) | Minimum Monitoring Frequency | Sample Location in the Distribution System |
| --- | --- | --- |
| SW/IGW 3 system serving ≥10,000 persons | Four water samples per quarter per treatment plant | At least 25 percent of all samples collected each quarter at locations representing maximum residence time. Remaining samples taken at locations representative of at least average residence time in the distribution system and representing the entire distribution system, taking into account number of persons served, different sources of water, and different treatment methods. 1 |
| SW/IGW 3 system serving 500 - 9,999 persons | One water sample per quarter per treatment plant | Locations representing maximum residence time. 1 |
| SW/IGW 3 system serving <500 persons | One sample per year per treatment plant during month of warmest water temperature | Locations representing maximum residence time. 1 If the sample (or average of annual samples, if more than one sample is taken) exceeds MCL, system must increase monitoring to one sample per treatment plant per quarter, taken at a point reflecting the maximum residence time in the distribution system, until system meets reduced monitoring criteria in 41.6(1)“c”(4)“2,” fourth unnumbered paragraph. |
| System using only non-IGW groundwater using chemical disinfectant and serving ≥10,000 persons | One water sample per quarter per treatment plant 2 | Locations representing maximum residence time. 1 |
| System using only non-IGW groundwater using chemical disinfectant and serving <10,000 persons | One sample per year per treatment plant during month of warmest water temperature | Locations representing maximum residence time. 1 If the sample (or average of annual samples, if more than one sample is taken) exceeds MCL, system must increase monitoring to one sample per treatment plant per quarter, taken at a point reflecting the maximum residence time in the distribution system, until system meets reduced monitoring criteria in 41.6(1)“c”(4)“2,” fourth unnumbered paragraph. |

1 If a system chooses to sample more frequently than the minimum required, at least 25 percent of all samples collected each quarter (including those taken in excess of the required frequency) must be taken at locations that represent the maximum residence time of the water in the distribution system. The remaining samples must be taken at locations representative of at least average residence time in the distribution system.

2 Multiple wells drawing water from a single aquifer may be considered one treatment plant for determining the minimum number of samples required, with department approval.

3 SW/IGW indicates those systems that use either surface water (SW) or groundwater under the direct influence of surface water (IGW), in whole or in part.

2. Reduced monitoring. The department may allow systems a reduced monitoring frequency, except as otherwise provided, in accordance with the following table. Source water total organic carbon (TOC) levels must be determined in accordance with 567—subparagraph 43.6(2)“c”(1).

Reduced Monitoring Frequency for TTHM and HAA5

| If you are a . . . | And you have monitored at least one year and your . . . | You may reduce monitoring to this level |
| --- | --- | --- |
| SW/IGW 1 system serving ≥10,000 persons which has a source water annual average TOC level, before any treatment, of ≤4.0 mg/L. | TTHM annual average ≤0.040 mg/L and HAA5 annual average ≤0.030 mg/L | One sample per treatment plant per quarter at distribution system location reflecting maximum residence time. |
| SW/IGW 1 system serving 500 - 9,999 persons that has a source water annual average TOC level, before any treatment, of ≤4.0 mg/L. | TTHM annual average ≤0.040 mg/L and HAA5 annual average ≤0.030 mg/L | One sample per treatment plant per year at distribution system location reflecting maximum residence time during month of warmest water temperature. |
| SW/IGW 1 system serving <500 persons | Any SW/IGW 1 system serving <500 persons may not reduce its monitoring to less than one sample per treatment plant per year. |
| System using only non-IGW groundwater using chemical disinfectant and serving ≥10,000 persons | TTHM annual average ≤0.040 mg/L and HAA5 annual average ≤0.030 mg/L | One sample per treatment plant per year at distribution system location reflecting maximum residence time during month of warmest water temperature. |
| System using only non-IGW groundwater using chemical disinfectant and serving <10,000 persons | TTHM annual average ≤0.040 mg/L and HAA5 annual average ≤0.030 mg/L for two consecutive years; or, TTHM annual average ≤0.020 mg/L and HAA5 annual average ≤0.015 mg/L for one year. | One sample per treatment plant per three-year monitoring cycle at distribution system location reflecting maximum residence time during month of warmest water temperature, with the three-year cycle beginning on January 1 following quarter in which system qualifies for reduced monitoring. |

1 SW/IGW indicates those systems that use either surface water (SW) or groundwater under the direct influence of surface water (IGW), in whole or in part.

● 	 Systems on a reduced monitoring schedule may remain on that reduced schedule as long as the average of all samples taken in the year (for systems which must monitor quarterly) or the result of the sample (for systems which must monitor no more frequently than annually) is less than or equal to 0.060 mg/L for TTHMs and is less than or equal to 0.045 mg/L for HAA5. Systems that do not meet these levels must resume monitoring at the frequency identified in 41.6(1)“c”(4)“1” in the quarter immediately following the quarter in which the system exceeds 0.060 mg/L for TTHMs and 0.045 mg/L for HAA5. For systems using only groundwater not under the direct influence of surface water and serving fewer than 10,000 persons, if either the TTHM annual average is >0.080 mg/L or the HAA5 annual average is >0.060 mg/L, the system must go to increased monitoring identified in 41.6(1)“c”(4)“1.”

● 	 The department may allow systems on increased monitoring to return to routine monitoring if TTHM annual average is less than or equal to 0.040 mg/L and HAA5 annual average is less than or equal to 0.030 mg/L.

● 	 The department may return a system to routine monitoring at the department’s discretion.

d.   	 Analytical requirements for disinfection byproducts.

(1) 	 Systems must use only the analytical method(s) specified in this paragraph, or equivalent methods as determined by EPA, to demonstrate compliance with the requirements of this rule.

(2) 	 Systems must measure disinfection byproducts by the methods (as modified by the footnotes) listed in the following table:

Approved Methods for Disinfection Byproduct Compliance Monitoring

| Methodology 2 | EPA | Standard | Byproduct measured 1 |
| --- | --- | --- | --- |
|  |  | Methods | TTHM | HAA5 | Chlorite 4 | Bromate |
| P&T/GC/EICD & PID | 502.2 3 |  | X |  |  |  |
| P&T/GC/MS | 524.2 |  | X |  |  |  |
| LLE/GC/ECD | 551.1 |  | X |  |  |  |
| LLE/GC/ECD |  | 6251 B |  | X |  |  |
| SPE/GC/ECD | 552.1 |  |  | X |  |  |
| LLE/GC/ECD | 552.2 |  |  | X |  |  |
| Amperometric Titration |  | 4500-ClO2E |  |  | X |  |
| IC | 300.0 |  |  |  | X |  |
| IC | 300.1 |  |  |  | X | X |

The procedures shall be done in accordance with the documents listed below. The incorporation by reference of the following documents was approved by the Director of the Federal Register on February 16, 1999, in accordance with 5 U.S.C. 552(a) and 1 CFR Part 51. Copies of the documents may be obtained from the sources listed below. Information regarding obtaining these documents can be obtained from the Safe Drinking Water Hotline at (800)426-4791. Documents may be inspected at EPA’s Drinking Water Docket, 401 M Street SW, Washington, DC 20460 (telephone: (202)260-3027); or at the Office of Federal Register, 800 North Capitol Street NW, Suite 700, Washington, DC.

The following method is available from the American Society for Testing and Materials, 100 Barr Harbor Drive, West Conshohoken, PA 19428:

Annual Book of ASTM Standards, Volume 11.01, American Society for Testing and Materials, 1996: Method D 1253-86.

The following methods are available from the National Technical Information Service, U.S. Department of Commerce, 5285 Port Royal Road, Springfield, VA 22161 (telephone: (800)553-6847):

“Determination of Inorganic Anions in Drinking Water by Ion Chromatography, Revision 1.0,” EPA-600/R-98/118, 1997 (available through

NTIS, PB98-169196): Method 300.1.

Methods for the Determination of Inorganic Substances in Environmental Samples, EPA-600/R-93/100, August 1993, (NTIS PB94-121811):

Method 300.0.

Methods for the Determination of Organic Compounds in Drinking Water—Supplement II, EPA-600/R-92-129, August 1992 (NTIS

PB92-207703): Method 552.1.

Methods for the Determination of Organic Compounds in Drinking Water—Supplement III, EPA-600/R-95-131, August 1995 (NTIS

PB95-261616): Methods 502.2, 524.2, 551.1, and 552.2.

The following methods are available from the American Public Health Association, 1015 Fifteenth Street NW, Washington, DC 20005:

Standard Methods for the Examination of Water and Wastewater, 19th edition, American Public Health Association, 1995: Methods: 4500-Cl D,

4500-Cl E, 4500-Cl F, 4500-Cl G, 4500-Cl H, 4500-Cl I, 4500-ClO2 D, 4500-ClO2 E, 6251 B, and 5910 B.

Standard Methods for the Examination of Water and Wastewater, Supplement to the 19th edition, American Public Health Association, 1996:

Methods: 5310 B, 5310 C, and 5310 D.

1 X indicates method is approved for measuring specified disinfection byproduct.

2ECD = electron capture detector IC = ion chromatography P&T = purge and trap

EICD = electrolytic conductivity detector LLE = liquid/liquid extraction PID = photoionization detector

GC = gas chromatography MS = mass spectrometer SPE = solid phase extractor

3 If TTHMs are the only analytes being measured in the sample, then a PID is not required.

4 Amperometric titration may be used for routine daily monitoring of chlorite at the entrance to the distribution system, as prescribed in

41.6(1)“c”(3)“1.” Ion chromatography must be used for routine monthly monitoring of chlorite and additional monitoring of chlorite

in the distribution system, as prescribed in 41.6(1)“c”(3)“2” and “3.”

(3) 	 Certified laboratory requirements. Analyses under this rule for disinfection byproducts shall only be conducted by laboratories that have been certified by the department and are in compliance with the requirements of 567—Chapter 83, except as specified under 41.6(1)“d”(4).

(4) 	 Daily chlorite samples at the entrance to the distribution system must be measured by a Grade II, III or IV operator meeting the requirements of 567—Chapter 81, any person under the supervision of a Grade II, III or IV operator meeting the requirements of 567—Chapter 81, or a laboratory certified by the department to perform analysis under 567—Chapter 83.

e.   	 Compliance requirements for disinfection byproducts.

(1) 	 General requirements.

1. 	 When compliance is based on a running annual average of monthly or quarterly samples or averages and the system fails to monitor for TTHM, HAA5, or bromate, this failure to monitor will be treated as a monitoring violation for the entire period covered by the annual average.

2. 	 Unless invalidated by the department, all samples taken and analyzed under the provisions of this rule must be included in determining compliance, even if that number is greater than the minimum required.

3. 	 If, during the first year of monitoring under paragraph 41.6(1)“c,” any individual quarter’s average will cause the running annual average of that system to exceed the MCL, the system is out of compliance at the end of that quarter.

(2) 	 Bromate. Compliance must be based on a running annual arithmetic average, computed quarterly, of monthly samples (or, for months in which the system takes more than one sample, the average of all samples taken during the month) collected by the system as prescribed by 41.6(1)“c”(2). If the average of samples covering any consecutive four-quarter period exceeds the MCL, the system is in violation of the MCL and must notify the public pursuant to 567—Chapter 42, in addition to reporting to the department pursuant to 567—paragraph 42.4(3)“d.” If a PWS fails to complete 12 consecutive months’ monitoring, compliance with the MCL for the last four-quarter compliance period must be based on an average of the available data.

(3) 	 Chlorite. Compliance must be based on an arithmetic average of each three-sample set taken in the distribution system as prescribed by 41.6(1)“c”(3)“1” and 41.6(1)“c”(3)“2.” If the arithmetic average of any three-sample set exceeds the MCL, the system is in violation of the MCL and must notify the public pursuant to 567—Chapter 42, in addition to reporting to the department pursuant to 567—paragraph 42.4(3)“d.”

(4) 	 TTHM and HAA5.

1. 	 For systems monitoring quarterly, compliance with MCLs in 41.6(1)“b” must be based on a running annual arithmetic average, computed quarterly, of quarterly arithmetic averages of all samples collected by the system as prescribed by 41.6(1)“c”(4).

2. 	 For systems monitoring less frequently than quarterly, systems demonstrate MCL compliance if the average of samples taken that year under the provisions of 41.6(1)“c”(4) does not exceed the MCLs in 41.6(1)“b.” If the average of these samples exceeds the MCL, the system must increase monitoring to once per quarter per treatment plant and is not in violation of the MCL until it has completed one year of quarterly monitoring, unless the result of fewer than four quarters of monitoring will cause the running annual average to exceed the MCL, in which case the system is in violation at the end of that quarter. Systems required to increase to quarterly monitoring must calculate compliance by including the sample that triggered the increased monitoring plus the following three quarters of monitoring.

3. 	 If the running annual arithmetic average of quarterly averages covering any consecutive four-quarter period exceeds the MCL, the system is in violation of the MCL and must notify the public pursuant to 567—Chapter 42 in addition to reporting to the department pursuant to 567—paragraph 42.4(3)“d.”

4. 	 If a PWS fails to complete four consecutive quarters of monitoring, compliance with the MCL for the last four-quarter compliance period must be based on an average of the available data.

f.   	 Reporting requirements for disinfection byproduct precursors. Systems required to sample quarterly or more frequently must report to the department within ten days after the end of each quarter in which samples were collected, notwithstanding the public notification provisions of 567— 42.1(455B). Systems required to sample less frequently than quarterly must report to the department within ten days after the end of each monitoring period in which samples were collected. The specific reporting requirements for disinfection byproducts are listed in 567—subparagraph 42.4(3)“d”(2).

41.6(2) Reserved.