661—205.20 (100) Ambulatory health care facilities.

205.20(1) New ambulatory health care facilities. NFPA 101, Life Safety Code, 2000 edition, Chapter 20, is adopted by reference as the fire safety rules for new ambulatory health care facilities.

205.20(2) Existing ambulatory health care facilities. NFPA 101, Life Safety Code, 2000 edition, Chapter 21, is adopted by reference as the fire safety rules for existing ambulatory health care facilities, with the following amendments:

Section 21.2.9.1 is not effective prior to March 13, 2006.

205.20(3) Alcohol-based hand rub dispensers. Notwithstanding any provisions of the 2000 edition of the Life Safety Code to the contrary, an ambulatory health care facility may place alcohol-based hand rub dispensers in its facility if:

a.   	 Use of alcohol-based hand rub dispensers does not conflict with a local code that prohibits or otherwise restricts the placement of alcohol-based hand rub dispensers in health care facilities;

b.   	 The dispensers are installed in a manner that minimizes leaks and spills that could lead to falls;

c.   	 The dispensers are installed in a manner that adequately protects against access by vulnerable populations; and

d.   	 The dispensers are installed in accordance with the following provisions:

(1) 	 Where dispensers are installed in a corridor, the corridor shall have a minimum width of 6 ft (1.8 m);

(2) 	 The maximum individual dispenser fluid capacity shall be:

1. 	 0.3 gallons (1.2 liters) for dispensers in rooms, corridors, and areas open to corridors;

2. 	 0.5 gallons (2.0 liters) for dispensers in suites of rooms;

(3) 	 The dispensers shall have a minimum horizontal spacing of 4 ft (1.2 m) from each other;

(4) 	 Not more than an aggregate 10 gallons (37.8 liters) of alcohol-based hand rub solution shall be in use in a single smoke compartment outside of a storage cabinet;

(5) 	 Storage of quantities greater than 5 gallons (18.9 liters) in a single smoke compartment shall meet the requirements of NFPA 30, Flammable and Combustible Liquids Code;

(6) 	 The dispensers shall not be installed over or directly adjacent to an ignition source; and

(7) 	 In locations with carpeted floor coverings, dispensers installed directly over carpeted surfaces shall be permitted only in sprinklered smoke compartments.